## RESULTS - Hole size
Leak Frequency per Segment |  | Gas | [5 empty] | Liquid
| Leak Scenario | NE | SM | ME | MA | LA | Total gas | NE | SM | ME | MA | LA
S3 | Full leak | 0.058929 | 0.0098842 | 0.0074393 | 0.0039439 | 0.0056418 | 0.085838 | 0 | 0 | 0 | 0 | 0
S3 | Limited leak | 0.033393 | 0.005601 | 0.0042156 | 0.0022349 | 0.003197 | 0.048641 | 0 | 0 | 0 | 0 | 0
S3 | Full pressure leak | 0.092322 | 0.015485 | 0.011655 | 0.0061787 | 0.0088388 | 0.13448 | 0 | 0 | 0 | 0 | 0
S8 | Full leak | 0.14017 | 0.023742 | 0.016571 | 0.01009 | 0.01424 | 0.20481 | 0 | 0 | 0 | 0 | 0
S8 | Limited leak | 0.079428 | 0.013454 | 0.0093903 | 0.0057177 | 0.0080695 | 0.11606 | 0 | 0 | 0 | 0 | 0
S8 | Full pressure leak | 0.21959 | 0.037196 | 0.025961 | 0.015808 | 0.02231 | 0.32087 | 0 | 0 | 0 | 0 | 0
S9 | Full leak | 0 | 0 | 0 | 0 | 0 | 0 | 0.002612 | 0.00043389 | 0.00036794 | 0.00015837 | 0.00028791
S9 | Limited leak | 0 | 0 | 0 | 0 | 0 | 0 | 0.010883 | 0.0018079 | 0.0015331 | 0.00065987 | 0.0011996
S9 | Full pressure leak | 0 | 0 | 0 | 0 | 0 | 0 | 0.013495 | 0.0022418 | 0.001901 | 0.00081824 | 0.0014875

## BasicInput
Hole size category | Size_min (mm) | Size_max (mm) | Correction factor, gas | Correction factor, liq
NE | 0 | 4 | 1 | 1 | 2.8284
SM | 4 | 7 | 1 | 1 | 5.7009
ME | 7 | 13 | 1 | 1 | 10.4403
MA | 13 | 25 | 1 | 1 | 19.9249
LA | 25 | 300000 | 1 | 1 | 25
[7 empty] | Table 4.5 | Typical gas leak rate [kg/s] – Leak smaller than 0.1 kg/s will be disregarded
Leak category | Time to detection [s] | Time to initiate ESD [s] | Valve closing time [s] | Time from isolation to blowdown [s] |  |  | Seg No. | Pressure (bara) | Small | Medium | Major | Large | Remark | Blowdown orifice [mm2] | D[mm]
Small | 60 | 30 | 30 | 180 |  |  | 1 | 1.05 | 0.000776 | 0.0807 | 0.257 | 0.517
Medium | 30 | 30 | 30 | 180 |  |  | 2 | 1.02 | 0.000314 | 0.0777 | 0.257 | 0.513
Major | 10 | 30 | 30 | 180 |  |  | 3 | Outlet:13 | 0.00863 | 0.214 | 0.704 | 1.41 |  | 12.84 | 7.1666
Large | 5 | 30 | 30 | 180 | 6.35 | 3.4817 | 8 | Outlet:151 | 0.00617 | 0.204 | 0.703 | 1.6 |  | 51.04 | 14.2885
[7 empty] | 9 | 4.01 | 0.0411 | 0.216 | 0.703 | 1.41
Note on D1: Amund Stokke: Insert factor to adjust frequencies within the category for example in accordance with historical data for the given installation. Detault value should be 1
Note on E1: Amund Stokke: Insert factor to adjust frequencies within the category for example in accordance with historical data for the given installation. Detault value should be 1